ED - UL re tank procedure is to send request to accredited UL engineer – would require destructive testing to certify tank – not an option

Instead have retained services naval engineering company Knude E Hansen out of Ft. Lauderdale

Prep for test – pump out & clean available for inspection Sept 5

Bheem - Email info to Elena Compton – company name and procedure

Ed Calculations for 110% containment will be certified – current detail short Jim Seavy to do - has draft and will have another sheet with calculations will be part of submittal

Will have aerial etc, for permit app.

Sept 28th anticipated date for permit application – Bheem says need tank alt procedure certified first Ed will have alt procedure submittal done by 28th instead.

Bheem Compton is lead – she needs to approve before application to modify can be submitted

Ed references Shop Fabricated Tanks standard engineer has seen and reviewed prior to

Penalty disc – ed asked about quantity est 8,000 gal oil from tank, exposure extimate <10 vs >10 emoploes Cost for economic benefit 0 Ed will submit counter offer

Asked about P2 SEP – can either approve before order is executed, or can wait - if have proposal will need Tallahassee review

Permit – closure cost discussion, other updates need to be done as they happen

10,000 gal tank content change only frac tank 20,000 gal alt procedure for sale off site

Tank table – adjust numbers and contents – can also make it an option for alternate content

Needs update to site plan, make it clearer with tanks numbered.

Tanks Registration 3 fuel, one frac

Ed – solid waste permit capital not available to do it correctly